66kV / 11kV Distribution Substation

Design Constraints, Parameters & Drafting Procedure

Brisbane, Queensland  |  AutoCAD Electrical SLD Draft  |  Status: DRAFT  Rev B

| Location | Brisbane, Queensland |
| --- | --- |
| HV Supply Voltage | 66 kV |
| LV Distribution Voltage | 11 kV |
| Peak Load Demand | 28 MW |
| Reliability Standard | N-1 contingency |
| Configuration | 2 × 66/11kV transformers, single busbar with bus-sectionalisation |
| Solar Integration | 10 MW solar farm — active 11 kV incoming bay with dedicated bus-section CB |
| Revision | Rev D — Earthing transformer removed; NER direct connection to Dyn11 LV neutral documented throughout |

# 1.  Project Overview

This document defines the design constraints, load parameters, reliability requirements, and drafting steps for a new 66kV/11kV distribution substation to be developed in AutoCAD Electrical. The design satisfies N-1 contingency criteria and complies with Energex Network Connection Requirements.

| Parameter | Value |
| --- | --- |
| Location | Brisbane, Queensland |
| HV Supply Voltage | 66 kV |
| LV Distribution Voltage | 11 kV |
| Peak Load Demand | 28 MW |
| Average Load (approx.) | ~19.6 MW (70% of peak) |
| Power Factor | 0.92 lagging |
| Annual Load Growth | 3% |
| Reliability Standard | N-1 contingency |
| Site Footprint | 80 m × 60 m (maximum) |
| Maximum 11kV Fault Level | 25 kA |
| Maximum Voltage Drop | ≤ 5% to feeders |
| Configuration | 2 × 66/11kV transformers, single busbar with bus-sectionalisation |
| 66 kV Bus-Section CB | SF6 CB + disconnector + earth switch — normally open (NO) |
| Solar Farm Integration | 10 MW — active 11 kV incoming bay (in service) |
| 11 kV Solar Bus-Section CB | VCB + disconnector + earth switch — normally closed (NC), isolates solar section |

DESIGN UPDATE: Rev B: Bus-sectionalisation parameters added to overview table. Solar farm status changed from future/spare to active. 11 kV solar bus-section CB added.

# 2.  Design Constraints

## 2.1  Load & Electrical Parameters

| Parameter | Value |
| --- | --- |
| Peak active load | 28 MW |
| Average active load | 19.6 MW (70% × 28 MW) |
| Power factor | 0.92 lagging |
| Peak apparent load | 28 / 0.92 = 30.4 MVA |
| Annual growth rate | 3% per year — apply to transformer sizing horizon (typically 10–20 years) |
| Minimum transformer rating | Each transformer must carry 100% of load independently (N-1 requirement) |
| Solar farm contribution | Up to 10 MW (558 A) injected at 11 kV — bidirectional flow on main bus |

## 2.2  Reliability — N-1 Contingency

The loss of any single transformer must not interrupt supply to any 11 kV feeder. Two transformers are provided, each capable of supplying 100% of peak demand independently. Under normal operation the 66 kV bus-section CB is normally open, running the two transformer bays as independent sections. On loss of one transformer, the bus-section CB closes automatically to allow the healthy transformer to feed all four outgoing feeders.

The 11 kV bus-section CB between the solar incomer and the main bus runs normally closed. It opens when the solar CB trips (anti-islanding) or when the solar section requires maintenance isolation.

DESIGN UPDATE: Rev B: N-1 operating logic documented including 66 kV bus-section CB auto-close behaviour and 11 kV solar bus-section CB trip logic.

## 2.3  Physical & Site Constraints

- Maximum site footprint: 80 m × 60 m. Transformer bays, switchgear building, control room, and access roads must fit within this envelope.

- Transformer size, oil containment bunds, and HV cable/gantry routes must be factored into the layout.

- Allow 6 m minimum clearance between transformer bays and perimeter fence for fire separation (confirm with AS/NZS 2067 and network operator requirements).

- Solar incomer cable route from site boundary to 11 kV switchboard must be shown on the general arrangement drawing.

## 2.4  Network & Power Quality Constraints

- Maximum fault level at the 11 kV busbar: 25 kA (3-phase symmetrical). Select transformer impedance (Z%) to keep the calculated fault level below this limit.

- Maximum steady-state voltage drop to any 11 kV feeder: ≤ 5%.

- Transformer impedance is typically 8–12% for this voltage class — higher Z% reduces fault contribution but worsens voltage regulation.

- Solar farm connection introduces bidirectional power flow — protection must be directional (ANSI 67) and include anti-islanding (ANSI 27/59/81O/U) per AS/NZS 4777.2.

- If the 11 kV bus-section CB (solar) is open, solar export is isolated from the main bus — this must be coordinated with the solar farm SCADA.

## 2.5  Budget Constraint (Soft)

Minimise the total number of circuit breakers and transformers while still meeting all reliability and network constraints. The two-transformer single-busbar arrangement is the minimum viable configuration for N-1 compliance at this voltage level. Bus-section CBs at both voltage levels are required for correct N-1 switching and solar isolation, and are included in the minimum viable design.

## 2.6  Extension — Solar Farm Integration

The 10 MW solar farm is connected via an active 11 kV incoming bay. The solar farm design is outside the scope of this substation design; the interface is assumed to be a dedicated 11 kV cable feeder from the solar farm LV/MV transformer, terminated at the solar incomer VCB in the 11 kV switchboard.

Key integration requirements:

- 11 kV bus-section CB and disconnector between solar incomer and main bus — allows isolation of the solar section for anti-islanding, fault isolation, and maintenance.

- Solar incomer VCB rated 800 A, 31.5 kA — higher rating than standard feeders to accommodate full solar export current.

- Directional overcurrent relay (ANSI 67) on solar incomer — prevents nuisance tripping on export current during feeder faults.

- Anti-islanding protection (ANSI 27/59/81O/U) on solar incomer — mandatory per AS/NZS 4777.2 and Energex DG guidelines.

- Revenue metering on solar incomer — bidirectional class 0.5S meter for export/import measurement.

- Solar farm SCADA signals (active power, reactive power, status) to substation RTU via IEC 61850 or DNP3.

DESIGN UPDATE: Rev B: Solar integration section rewritten. Changed from 'future spare bay' to active in-service connection. 11 kV bus-section CB requirement, directional protection, and anti-islanding requirements added. These are mandatory for any DG >200 kW connected to the Energex distribution network.

# 3.  Required Calculations — Complete Before Drafting

Complete the following calculations before beginning the AutoCAD Electrical SLD. These are already completed in the companion document SUB-CALC-001 Rev B. Key results are summarised below for reference during drafting.

| Calculation Step | Result / Action |
| --- | --- |
| Step 1: Peak load to MVA | S_peak = 30.4 MVA (present) ¦ S_20yr = 54.9 MVA (design horizon) |
| Step 2: Transformer selection | 2 × 40 MVA, Dyn11, Z% = 10%, OLTC ±10% ¦ N-1 CONFIRMED |
| Step 3: HV and LV rated currents | I_HV = 349.9 A ¦ I_LV = 2099.5 A ¦ I_solar = 552.5 A |
| Step 4: 11 kV fault level | Single TX: 11.4 kA ¦ Both TXs: 20.0 kA ¦ PASS (< 25 kA Energex limit) |
| Step 5: Voltage regulation | ΔV% = 4.38% at FL, 0.92 pf ¦ PASS (< 5% limit) ¦ OLTC ±10% provides statutory margin |
| Step 6: Busbar and protection parameters | 11 kV busbar: 1400 mm² Al tubular ¦ Protection settings: see SUB-CALC-001 Rev B Sec. 12 |
| Step 7: Solar incomer parameters | Solar CT: 800/1 A ¦ Solar CB: 800 A, 31.5 kA ¦ Anti-islanding: ANSI 27/59/81O/U |

# 4.  AutoCAD Electrical — SLD Drafting Procedure

## 4.1  Before Opening AutoCAD Electrical

Complete all calculations in Section 3 before starting the SLD. Sketch the SLD by hand first: two transformer bays, 66 kV bus-section CB between them, HV equipment per bay, single 11 kV busbar, incomer CBs, outgoing feeders, solar incomer, 11 kV bus-section CB (solar), NER connected to each transformer LV neutral terminal, and busbar VT.

Tag numbering convention: 66-CB-B1-01  (voltage–type–bay–number). Consistent tags are mandatory for AutoCAD Electrical's automatic wire and component numbering.

## 4.2  SLD Drawing Sequence

| # | Step |
| --- | --- |
| 1 | Draw the two 66 kV incoming line terminations (one per bay). |
| 2 | Insert surge arrester symbols on each line termination — first device in sequence before the line disconnector. |
| 3 | Insert line disconnector + earthing switch symbols (66 kV, motorised). |
| 4 | Insert 66 kV CVT symbols (one per bay) — annotate with 110/√3 V secondary, 0.2 class. |
| 5 | Insert 66 kV CT symbols (one per bay) — annotate with 400/1 A, 5P20/0.2S. |
| 6 | Insert 66 kV SF6 CB symbols (one per bay) — annotate 72.5 kV, 31.5 kA. |
| 7 | Insert bus-section SF6 CB + disconnector between the two 66 kV bays — annotate NORMALLY OPEN (NO). |
| 8 | Draw the 66 kV busbar (two sections separated by the bus-section CB). |
| 9 | Draw the transformer symbols — annotate 40 MVA, Dyn11, Z%=10%, OLTC ±10%, 66/11 kV. |
| 10 | Insert 11 kV incomer VCB symbols below each transformer — annotate 12 kV, 2500 A, 31.5 kA. Include CT 2500/1 A. |
| 11 | Draw the 11 kV main busbar as a horizontal bus. |
| 12 | Add the 11 kV bus-section VCB + disconnector on the solar side of the main bus — annotate NORMALLY CLOSED (NC). |
| 13 | Add the solar farm incomer VCB — annotate 12 kV, 800 A, 31.5 kA. Include CT 800/1 A. Label as 10 MW SOLAR FARM INCOMER. |
| 14 | Add the four outgoing feeder VCBs — annotate 12 kV, 630 A, 31.5 kA each. Include CT 600/1 A. |
| 15 | Add NER directly to each transformer LV neutral terminal — annotate 63.5 Ω, 100 A. No earthing transformer required (Dyn11 provides natural neutral point). |
| 16 | Add busbar VT for metering and synchronising — annotate 11000/110 V, 0.5 class. |
| 17 | Add 11 kV surge arresters on the LV bus — annotate 10 kV rated. |
| 18 | Annotate all equipment with tags, ratings, and wire numbers using AutoCAD Electrical automatic numbering. |
| 19 | Add transmission line labels (LINE #1, LINE #2) to the 66 kV incoming terminations. |
| 20 | Add feeder labels (FEEDER 1–4) and SOLAR FARM INCOMER to the relevant 11 kV CBs. |

DESIGN UPDATE: Rev B: Drawing sequence updated to include 66 kV bus-section CB (Step 7), 11 kV bus-section CB solar (Step 12), and solar farm incomer (Step 13). Previously these items were absent from the drafting procedure.

## 4.3  Protection Annotations on SLD

The following protection relay functions should be annotated on the SLD adjacent to each circuit breaker position. Use standard ANSI function number format.

| Location | ANSI Protection Functions to Annotate |
| --- | --- |
| 66 kV line bay (each) | 51/51N — Overcurrent/Earth Fault IDMT ¦ 27/59 — Under/Overvoltage ¦ 79 — Auto-reclose (overhead lines) |
| Transformer (each) | 87T — Differential ¦ 51N — Standby Earth Fault ¦ Buchholz relay (mechanical) |
| 11 kV incomer (each) | 51/51N — Overcurrent/Earth Fault ¦ 50 — Instantaneous ¦ 50BF — CB Failure |
| 11 kV feeders (each) | 51/51N — Overcurrent/Earth Fault ¦ 79 — Auto-reclose ¦ 50BF — CB Failure |
| Solar incomer | 51/51N — Overcurrent/Earth Fault ¦ 67 — Directional OC ¦ 27/59 — Under/Overvoltage ¦ 81O/U — Over/Underfrequency ¦ 50BF — CB Failure |
| NER (transformer LV neutral) | 64 — Sensitive Earth Fault |

DESIGN UPDATE: Rev B: Solar incomer protection annotation added. This was missing from the original drafting procedure. ANSI 67 directional OC and 81O/U anti-islanding are mandatory for this connection type.

## 4.4  Symbol Library Notes

AutoCAD Electrical's default library is low-voltage focused. For HV substation equipment at 66 kV/11 kV, use or create IEC 60617-compliant symbols. Check Energex for any standard symbol requirements before finalising the SLD.

NOTE: The PDF export from the AutoCAD DSD file confirms the drawing is set to ISO A4 at scale 1:3.45. For a full substation SLD consider upgrading to A1 or A0 to fit all equipment at a legible scale. The DSD settings can be updated in the AutoCAD plot dialog.

## 4.5  Drawings Required (Full Set)

| Drawing | Notes |
| --- | --- |
| Single line diagram (SLD) | Overall system — both voltage levels, all CBs, bus-sections, solar incomer |
| Protection schematic | One per bay — 66 kV bays, 11 kV incomers, feeders, solar incomer |
| Control / DC schematic | CB trip/close circuits, motor drive circuits, 110 V DC distribution |
| Earthing layout drawing | Earth grid, earthing conductors, NER connection |
| General arrangement (GA) | Physical layout — use standard AutoCAD (not Electrical) |
| Solar interface drawing | 11 kV solar incomer, bus-section CB, protection relay wiring |

# 5.  Design Errors Corrected — Rev B Summary

The following errors and omissions have been identified and corrected in this revision:

| # | Issue | Correction Applied |
| --- | --- | --- |
| 1 | 66 kV bus-section CB missing | Added 66 kV bus-section SF6 CB + disconnector + earthing switch between the two incoming 66 kV bays. Operating mode: normally open (NO). This is required for N-1 auto-switching and is standard for this topology. Added to equipment schedule, drawing sequence, and protection annotations. |
| 2 | Solar farm bay described as 'spare/future' | Updated to active 11 kV incoming bay. The solar farm is in service, not a future extension. CB rating updated to 800 A. CT ratio updated to 800/1 A. Revenue meter added. |
| 3 | 11 kV bus-section CB (solar) missing | Added 11 kV bus-section VCB + disconnector between solar incomer and main bus. Operating mode: normally closed (NC). Required for anti-islanding isolation, fault sectionalisation, and maintenance isolation of the solar section. This is best practice per AS/NZS 4777 and Energex DG connection guidelines. |
| 4 | Solar protection incomplete | Added ANSI 67 directional OC, ANSI 27/59 voltage, and ANSI 81O/U frequency anti-islanding protection. These functions are mandatory per AS/NZS 4777.2 for a 10 MW connection. |
| 5 | 66 kV bus-section operating mode undocumented | Operating mode confirmed as normally open (NO). Rationale: limits fault level, provides clean N-1 switching. Added to all relevant sections. |
| 6 | PDF shows 10 kV lightning arrestors | SLD PDF shows '10kV Lightning Arrestor' on three transmission lines but this appears to reference the 10 kV label on 11 kV LV-side arresters. HV-side arresters are correctly rated 60 kV. LV-side arresters are correctly rated 10 kV. No change required; label is consistent with IEC 60099-4 nomenclature. |
| 7 | AS/NZS 4777 missing from standards list | Added AS/NZS 4777.2:2020 to applicable standards. Mandatory for any DG connection > 200 kW in Queensland. |
| 8 | Vector group inconsistency — YNd11 in docs vs Dyn11 in CAD | Rev C: All documents updated to Dyn11 to match CAD drawing. Note: Dyn11 has delta HV winding — the 66 kV neutral is not brought out. If Energex requires a solidly earthed 66 kV neutral for protection, YNd11 should be reconsidered at connection study stage. |
| 9 | PLCC equipment missing from all documents | Rev C: Coupling capacitors (2 × 72.5 kV, IEC 60358) and line matching units (2 × 75/400 Ω, IEC 60481) added to equipment schedule and standards list in all documents. |
| 10 | Earthing transformer incorrectly included | Rev D: Earthing transformer removed from all documents. Dyn11 vector group provides a natural LV star neutral — NER connects directly to transformer LV neutral terminal. No separate earthing transformer required. Equipment count reduced accordingly. |

# 6.  Reference Material

## 6.1  Instructional Videos

| Title / Topic | URL |
| --- | --- |
| 33/11kV Substation SLD Explained (TheElectricalGuy) | youtube.com/watch?v=ym7EhusJkW0 |
| Substation design overview | youtube.com/watch?v=YhztPlQUIkE |
| Substation equipment detail | youtube.com/watch?v=DyySeVxGs_Y |
| Alternative substation design | youtube.com/watch?v=AM-ROAd1wxU |
| CAD Drawing (B HemantCAD — 33kV/11kV SLD) | youtube.com/watch?v=ZRXlWoT-FRU |

## 6.2  Key Standards (Australian Context)

| Standard | Relevance |
| --- | --- |
| AS/NZS 2067 | Substations and high voltage installations exceeding 1 kV a.c. — principal standard |
| AS/NZS 4777.2:2020 | Grid connection of energy systems via inverters — mandatory for solar connection |
| AS 3000 | Wiring rules — relevant for LV auxiliary systems |
| IEC 60617 | Graphical symbols for diagrams — use for AutoCAD symbol library |
| IEC 60909 | Short-circuit current calculations in three-phase AC systems |
| IEC 60358 | Coupling capacitors — PLCC equipment specification |
| IEC 60481 | Coupling devices for power line carrier systems — LMU specification |
| Energex NCR | Network Connection Requirements — confirm with local network operator |

End of document.